## Slide 1
Dr.Sc.ing. Kamila Gruškeviča
Riga Technical University
www.wrl.bf.rtu.lv
Drinking water quality effect on the corrosion of the cast iron pipes

## Slide 2
Environmental conditions

## Slide 3: Iron Corrosion types
uniform
galvanic
tuberculation

## Slide 4
Corrosion related problems:
Increase of pumping costs due to increase of pipe wall roughness and water turbidity;

## Slide 5
Corrosion related problems:
Water loss because of leakages;
Damage or pipes and armatures because of water aggressiveness

## Slide 6
Corrosion related problems:
Necessity of increase of chlorine doses to maintain regulatory amount of residual chlorine;

## Slide 7
Corrosion related problems:
Increase of costs of wastewater treatment and handling.

## Slide 8: The corrosion of steel in case of closely located anode and cathode
Notes: Metāla oksidācija un noārdīšana notiek uz anoda. Elektroni, kas atbrīvojas anoda reakcijas dēļ, pārvietojas uz katodu, kur viņi pāriet pie akceptora, piemēram, skābekļa. Pozitīvos jonus, kas ģenerējas uz anoda, pievelk katods un otrādi. Šī migrācija notiek kā koncentrācijas gradientu maiņas rezultāts, lai uzturētu elektriski neitrālu vidi.

## Slide 9: Factors affecting corrosion:
Dissolves gasses, especially oxygen;
Dissolved and suspended solids and particles;
pH;
alkalinity;
hardness;
temperature;
water flow velocity;
microbiological activity.

## Slide 10
Corrosion – what is inside?

## Slide 11: Corrosion process

## Slide 12: Corrosion indexes
Langelier saturation index (LI) indicates the posibility of solubility or precipitation of calcium carbonate in water systems.
LSI > 0 Water is oversaturated and CaCO3 precipitates.
LSI = 0 Equilibrium conditions.
LSI < 0 Water is unsaturated and no protective layer can be formed.

## Slide 13
The Larson-Skold index describes the corrosivity of water towards mild steel
LR < 0,8 Chlorides and sulfates do not affect the formation of natural protective layer.
0,8 < LR <1,2 Chlorides and sulfates may interfere with natural film formation. Higher than usual corrosion rates.
LR > 1,2 The tendency towards high corrosion rates of a local type should be expected.

## Slide 14: Corrosion experiments
Flow rate
B1 0.35 m/s
B2 0.05 m/s
B3 0.35 / 0 m/s
B4 0.35 / 0.05 m/s

## Slide 16: Example 1 (LSI = 0.7)
Weight changes, %
Time, days

## Slide 17: coupons
Parameter | Average (n=12)
pH | 7,57
Ca, mg/L | 63,36
Alkalinity, mmol/L | 3,01
Temperature, °C | 10,62
Sulfate, mg/L | 61,09
Chlorides, mg/L | 117,5
EC, µS/cm2 | 754
Turbidity, NTU | 0,54
RedOx, mV Ag/Cl | 257,82

## Slide 18: Example2 (LSI = -0.1)
Weight changes, %
Time, days

## Slide 19: Coupons
Parameter | Average (n=12)
pH | 6,91
Ca, mg/L | 52,13
Alkalinity, mmol/L | 2,13
Temperature, °C | 8,65
Sulfates, mg/L | 121,81
Chlorides, mg/L | 7,47
EC, µS/cm2 | 358
Turbidity, NTU | 0,195
RedOx, mV Ag/Cl | 260

## Slide 21: Example 3 (LSI = -0.36)
Weight changes, %
Time, days

## Slide 22: coupons
Parameter | Average (n=12)
pH | 7,52
Ca, mg/L | 67,56
Alkalinity, mmol/L | 4,17
Temperature, °C | 13,31
Sulfates, mg/L | 182
Chlorides, mg/L | 30,4
EC, µS/cm2 | 901
Turbidity, NTU | 0,54
RedOx, mV Ag/Cl | 267

## Slide 23: Oxygen diffusion in different flow conditions

## Slide 24
Thank you for your attention!
Tallinn
20.05.2016