## Slide 1
Dr.Sc.ing., assoc.proff. Jānis Rubulis
Riga Technical university
www.wrl.bf.rtu.lv/en/
janis.rubulis@rtu.lv
mob.phone.+37129438018
Drinking water network flushing: tool to save water quality
BALTIC WATER WORKS CONFERENCE 2016
Tallink M/S Victoria I
19.05.2016

## Slide 2: DN 100-200 network flushing
Effective
World-wide used
Tested In latvia
Notes: I can help

## Slide 3: structure of presentation
Problem definition
Solution – unidirectional flushing
Experience
costs
chalenges and future trends

## Slide 4
Problem definition

## Slide 5: Discoloraton Complain statistics
www.wired.com
Riga: 0.07 complain/1000 consumers/year
Netherlands: 0.5-1 complain /1000 consumers/year
UK: 4 complain /1000 consumers/year
Australia: 1.1-17.9 complain / consumers/year
Zabašta et al, 2014; WSAA Facts 2005
60-80% Australia (Rayan et. al 2003)
80% Japan (Matsui et. al 2007)
70% Latvia (Neilands et al, 2009)
80% UK (Husband and Boxall 2011)

## Slide 6: Customers interviews
Concern about Tap Water
Consumers use tap water for drinking, but they boil it before use, resulting in perception that it is “safer”.
They feel that good water is spoiled by the old, bad quality water pipes.

## Slide 7
Vreeburg un Boxall, 2007
Complains
reviewed
confirmed

## Slide 8: Customers interviews
Relations Between the Consumer and the Water Supplier
Customers feel that they receive little information from their supplier.

## Slide 9: chemical parameters in 2013
http://www.vi.gov.lv
Iron
Turbidity
Sulphates
Manganese
Taste, smell
Other
Notes: Veselības inspekcija, 2014
2013. gada ķīmisko rādītāju neatbilstības, rādītāju dinamika un dzelzs koncentrācija Latvijā

## Slide 10
Cause
Chart: Year
| 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010
uzņēmuma "Stokholmas ūdens " prognozes ('90.gadu vidū) | 362 | 331 | 308 | 295
kompānijas "Rust VA-Projekt" prognozes ('90.gadu vidū) | 408 | 378 | 345 | 330 | 327 | 338
padeve | 360 | 314 | 271 | 221 | 191 | 154 | 147 | 130
Notes: 10

## Slide 11: Customers interviews
Attitudes Towards the Water Supplier
In order to increase the efficiency of the work, they think that water suppliers should change the old water pipes and to check the water quality on the regular basis.

## Slide 12
Solution – unidirectional flushing

## Slide 13: Procedure
Clean water front;
Minimal flow velocity 1.5 m/s;
Volume to be flushed: 2.
Notes: Manipulējot ar aizbīdņiem un pakāpeniski skalojot ūdensvadu no attīrīšanas stacijas līdz tālākajam punktam
Minimālo ātrumu bieži arī nesanāca sasniegt, mazajiem diametriem galvenokārt spiediena zudumu dēļ, bet lielajiem diametriem arī iekārtu dēļ, kuras pievienotas ar 64mm neatļāva sasniegt lielāku caurplūdumu.
Centās skalot 2-3 caurules garumus (tilpumus), bet ja duļķainība bija augsta plūsmu nedaudz pakāpeniski piegriēza.

## Slide 14
Procedure
Measurements:
Flow → velocity,
Turbidity
Notes: 14

## Slide 15
© J.H.G. Vreeburg
Hydraulic model is optional
Selfcleaning networks v>0,4m/s (Blokker et al 2010)
Notes: 15
The need for Hydraulic model is optional: Known velocities and critical locations

## Slide 16
Turbidity monitoring at station
Notes: 16

## Slide 17
experience

## Slide 18: Netherlands (Watercycle Research Institute - KWR) and germany (Technologiezentrum Wasser - TZW)

## Slide 19
2008-2009
Ādaži
Rīga
Notes: 19

## Slide 20
SIA Jelgavas water
Notes: Tehniskais direktors Viktors Juhna, ūdens apgādes dienesta vadītājs Guntis Ābols, ražošanas tehniskās nodrošināšanas dienests Raimonds Mekša, Jānis Šeskens

## Slide 21
 | 2013 | 2014 | 2015
Flushed pipes, km | 84.2 | 85.2 | 79.05
Water for flushing, m3 | 8713.5 | 5337.4 | 3862.1
Time spent for flushing, h | 208 | 99 | 75
Flushed sediments (dry matter), kg | 286 | 273 | 120
Flushed sediments (dry matter), g/m | 3.4 (9.6) | 3.2 | 1.5
2015 vs 2013: 2x less water, 3x less time
2015: 2x more sediments in CI than PE
Notes: Trials in a plastic only network with particle-free water produced by 0.1mm ultra-filtration demonstrated that particles responsible for discolouration can originate solely from the supplied water (Vreeburg et al., 2008).

## Slide 22: Expected costs

## Slide 23
Used water - 2 volumes from the pipe length (±10-15%).
Staff: 2
1 car
time: 4h for 1km
Amortization of instruments used for flushing

## Slide 24: Customers interviews
Payment
Generally, consumers would wish to pay less for their water. The money paid for water is considered as corresponding to the water quality. The respondents would be ready to pay more for water, if the tap water would have excellent taste qualities.

## Slide 25: Challenges and future trends
Water safety plan →Autumn 2017

## Slide 26: design principles in Latvia and the Netherlands
 | Latvia | Netherlands
Water supply continuity | Depending on the population | Interruption is not allowed
Type of networks | looped/branched | branched
Minimum flow velocity | Not defined | 0,40 m/s
Minimum pressure at the consumer | 0,1 MPa | 0,2 MPa
Fire hydrant connection, capacity | Ø 110 mm | Ø 63 mm 30 m3/h instead of 90 m3
self-cleaning networks
(Vreeburg et al 2009)
Notes: Darbā tika analizēti projektēšanas principi Latvijā un Nīderlandē. Nīderlande praksē ir ieviesusi pašaatīrošo tīklu projektēšanu, kur minimāla spiediena, piegādes nepārtrauktības, ugunsdzēsības ūdens plūsmas prasībām un dzeramā ūdens kvalitātes prasībām pievienots vēl piektais kritērijs – ātruma, kritērijs, kurš nodrošina dzeramā ūdensapgādes tīklu pašattīrīšanos, līdz ar to izslēdzot mikroorganismu veidošanos.

## Slide 27
Acknowledgements
Kaspars Neilands, PhD student.
Ivars Šarenkovs, M.Sc.
Adazi udens Ltd., Jelgavas udens Ltd. and Rigas udens Ltd
www.wrl.bf.rtu.lv/en/
Notes: 27

## Slide 28: Customers interviews
Bottled Water Consumption
consumed on a daily basis. In comparison to tap water, bottled water is considered to be cleaner, it does not have sediments and it is tastier. However, it is considered to be expensive.
Due to poor drinking water quality resulting from the pipe networks, it is assumed that consumers do not trust their tap water quality, often leading them to purchase bottled water.

## Slide 29
Notes: take-home message
it is assumed that consumers do not trust their tap water quality, often leading them to purchase bottled water.
consumed on a daily basis. In comparison to tap water, bottled water is considered to be cleaner, it does not have sediments and it is tastier. However, it is considered to be expensive.

## Slide 30
Dr.Sc.ing., assoc.proff. Jānis Rubulis
Riga Technical university
www.wrl.bf.rtu.lv/en/
janis.rubulis@rtu.lv
mob.phone.+37129438018
Drinking water network flushing: tool to save water quality
BALTIC WATER WORKS CONFERENCE 2016
Tallink M/S Victoria I
19.05.2016
Thank you!

## Slide 31: MOTIVĀCIJA

## Slide 32: Flushed sediments (dry matter), g/m
0.003-0.052 – Australia (Rayan et al 2008)
0.027-0.23 – Netherlands (with ultrafiltratition) (Vreeburg et al 2008)
0.26 - 0.4 – Canada (Barebout-Benoit et al 2005)
0.053-3.1 – Netherlands (Vreeburg et al 2008)
1.5 - 3 (9.6) – Jelgava (2013-2015)
Up to 12 – France (Harmant et al.2000)
0.3 – 24 – Canada (Carriere et al. 2005)
0.08 - 50 – USA (Delanoue et al, 1997)
Notes: The concentration of particles in Latvian DWN is higher compared to others countries (Canada, Netherlands, UK)

## Slide 33: > DN 250
www.hammann-gmbh.de

## Slide 34
Husband et al 2011, UK
500 l/s (1.35 m/s)
Severn Trent Water
Notes: 13.3 km long 700 mm (27”) diameter lined steel trunk main had been run with only a sweetening ‘trickle’ flow of around 15 l/s or 0.04 m/s. Due to the volumes of water required during flushing and the likelihood of significant material being mobilised, discharge was planned into storm tanks at a waste water treatment plant adjacent to the trunk main at 10 km along its length. To facilitate this a temporary 500 mm connection was fitted and this was linked to ten 150 mm ‘flushing hoses’, Figure.

## Slide 35
Daļiņu raksturojums
Kvarcs SiO2 Getīts FeO(OH) Alunīts AlSO4·H2O
Kvarcs SiO2 Getīts FeO(OH)
Getīts FeO(OH)
Laboratoriski analizēts daļiņu ķīmiskais sastāvs kopumā no 24 paraugiem
Izskaloto daļiņu vidējie diametri ir robežās no <1 μm līdz 619 μm (n=28).
Notes: 35

## Slide 37
Experience in Latvia
AR – mākslīgi papildināts pazemes ūdens, CI – kaļamais ķets, G – pazemes ūdens, PE - polietilēns,
PVC - polivinilhlorīds, S – virszemes ūdens, UI - tērauds, WTP- ūdens attīrīšanas stacija

## Slide 38
http://www.rtu.lv/content/view/5047/1837/lang,lv/

## Slide 39
Notes: Consumption trends

## Slide 40
Drinking water counting Rubulis (2002)